## Method
Minimum fault current If,min of the recloser zones (DG out of service)
Software | DIgSILENT PowerFactory 2021, IEEE 13-node feeder model (project IEEE13 DSDR Fuse Coordination)
Calculation | Short circuit, complete method (pre-fault load flow included), initial symmetrical current Ikss
Fault | Line-to-ground (LG) through a fault resistance Rf = 3 ohm
Locations | Every node of the zone and every phase present at that node
DG | Out of service (the pickup is designed without DG)
Current read | Current through the recloser = largest of its three phase currents (fault current + load current, added as phasors, because the complete method keeps the load flowing)
R1 zone | 632, 633, 645, 646, DL, 671, 692, 675, 680, 684, 652, 611
R2 zone | 671, 692, 675, 680, 684, 652, 611 (downstream of R2)
If,min | Lowest recloser current over all LG 3-ohm faults of the zone -> =MIN(IF(...)) in sheet If_min_R1_R2
Pickup check | The pickup must be below If,min, so that the recloser still detects the weakest fault of its zone
Why If,min is not at the farthest node | The farthest node (652) gives the smallest current AT THE FAULT, but the recloser also carries the load current of its phase. The smallest RECLOSER current is therefore at 680 on phase B, the phase with the smallest sum of load and fault current.

## LG_3ohm_faults
Faulted node | Faulted phase | Rf (ohm) | Current at the fault (A) | Current through R1 (A) | Current through R2 (A) | In R1 zone | In R2 zone
632 | A | 3 | 742.9 | 1237.1 | 444 | yes | no
632 | B | 3 | 777.3 | 1149.9 | 465 | yes | no
632 | C | 3 | 739.2 | 1265.8 | 467.4 | yes | no
633 | A | 3 | 721.2 | 1214.8 | 443.2 | yes | no
633 | B | 3 | 754.4 | 1125.1 | 465.3 | yes | no
633 | C | 3 | 718.3 | 1244.4 | 467.4 | yes | no
634 | A | 3 | 91.3 | 587.7 | 469.8 | no | no
634 | B | 3 | 95.8 | 587.7 | 469.9 | no | no
634 | C | 3 | 91.5 | 596.7 | 470 | no | no
645 | C | 3 | 705.5 | 1234.4 | 467.6 | yes | no
645 | B | 3 | 739.6 | 1109.8 | 465.4 | yes | no
646 | C | 3 | 686.2 | 1216.4 | 467.8 | yes | no
646 | B | 3 | 719.5 | 1090.1 | 465.6 | yes | no
671 | A | 3 | 667.9 | 1151.6 | 1078.8 | yes | yes
671 | B | 3 | 728.5 | 1101.6 | 907.4 | yes | yes
671 | C | 3 | 658.8 | 1176.9 | 1032.2 | yes | yes
692 | A | 3 | 667.9 | 1151.6 | 1078.8 | yes | yes
692 | B | 3 | 728.5 | 1101.6 | 907.4 | yes | yes
692 | C | 3 | 658.8 | 1176.9 | 1032.2 | yes | yes
675 | A | 3 | 646.2 | 1128 | 1054.5 | yes | yes
675 | B | 3 | 711.3 | 1085.4 | 890.3 | yes | yes
675 | C | 3 | 640.4 | 1157.6 | 1012 | yes | yes
680 | A | 3 | 644.5 | 1129.9 | 1056.4 | yes | yes
680 | B | 3 | 701.5 | 1074.4 | 878.5 | yes | yes
680 | C | 3 | 635.5 | 1154.7 | 1007.6 | yes | yes
684 | A | 3 | 650.1 | 1134.1 | 1060.8 | yes | yes
684 | C | 3 | 640.3 | 1158.9 | 1013 | yes | yes
652 | A | 3 | 617.2 | 1102.4 | 1028.3 | yes | yes
611 | C | 3 | 622.7 | 1141.7 | 994.8 | yes | yes
DL | A | 3 | 703.9 | 1193.5 | 433.2 | yes | no
DL | B | 3 | 752.1 | 1125.1 | 461.2 | yes | no
DL | C | 3 | 697.1 | 1219.5 | 471.1 | yes | no
Yellow: the lowest recloser current of each zone (If,min).
Node 634 is behind the 4.16/0.48 kV transformer: in no recloser zone for this check (its own section is XFM-1).

## If_min_R1_R2
Recloser | Zone (nodes) | Farthest node | Current at the fault, farthest node (A) | Recloser current, farthest node (A) | If,min = lowest recloser current in the zone (A) | Node of If,min | Phase of If,min | Inom (A) | Ip = 1.25 x Inom (A) | Pickup applied (A) | Setting | Check: pickup < If,min
R1 | 632, 633, 645, 646, DL, 671, 692, 675, 680, 684, 652, 611 | 652 | 617.2 | 1102.4 | 1074.4 | 680 | B | 587.7 | 734.6 | 720 | CT 900/5, tap 4 A | OK: 720 < 1074.4
R2 | 671, 692, 675, 680, 684, 652, 611 | 652 | 617.2 | 1028.3 | 878.5 | 680 | B | 470 | 587.5 | 600 | CT 1000/5, fast plug 300 A (curve from 600 A) | OK: 600 < 878.5
How each value is obtained (sheet LG_3ohm_faults holds the data):
Column | Excel formula (R1 row; R2 uses column F / H instead of E / G)
D current at the fault, farthest node | =MIN(IF(LG_3ohm_faults!$A$2:$A$33=C2,LG_3ohm_faults!$D$2:$D$33)) (array formula: Ctrl+Shift+Enter)
E recloser current, farthest node | =MIN(IF(LG_3ohm_faults!$A$2:$A$33=C2,LG_3ohm_faults!$E$2:$E$33)) (array)
F If,min | =MIN(IF(LG_3ohm_faults!$G$2:$G$33="yes",LG_3ohm_faults!$E$2:$E$33)) (array)
G node of If,min | =INDEX(LG_3ohm_faults!$A$2:$A$33,MATCH(1,(LG_3ohm_faults!$E$2:$E$33=F2)*(LG_3ohm_faults!$G$2:$G$33="yes"),0)) (array)
H phase of If,min | =INDEX(LG_3ohm_faults!$B$2:$B$33,MATCH(1,(LG_3ohm_faults!$E$2:$E$33=F2)*(LG_3ohm_faults!$G$2:$G$33="yes"),0)) (array)
J pickup by eq. (3) | =1.25*I2
M check | =IF(K2<F2,"OK","NOT OK")
Values from the PowerFactory database: R1 If,min 1074.4 A and R2 If,min 878.5 A, both for the LG fault through 3 ohm at 680, phase B.

## All_sections
Protection section | Farthest node | Line length to it (ft) | Fault type | Faulted phase | Rf (ohm) | Current at the fault (A) | Section current, fault at the farthest node (A) | Lowest LG 3-ohm section current (If,min)
RG60-632 | 652 | 5100 | LG | A | 3 | 617.2 | 1102.4 | 1074.4 A (fault at 680, phase B)
632-633 | 633 | 500 | LG | C | 3 | 718.3 | 760.2 | 760.2 A (fault at 633, phase C)
632-645 | 646 | 800 | LG | C | 3 | 686.2 | 728.4 | 728.4 A (fault at 646, phase C)
632-671 | 652 | 1100 | LG | A | 3 | 617.2 | 1028.3 | 878.5 A (fault at 680, phase B)
XFM1-HV-side | 634 | 0 | LG | B | 3 | 95.8 | 81.0 | 81.0 A (fault at 634, phase B)
XFM1-LV-side | 634 | 0 | LG | B | 3 | 95.8 | 706.0 | 706.0 A (fault at 634, phase B)
645-646 | 646 | 300 | LG | C | 3 | 686.2 | 728.4 | 728.4 A (fault at 646, phase C)
671-692 | 675 | 500 | LG | B | 3 | 711.3 | 735.0 | 735.0 A (fault at 675, phase B)
671-684 | 652 | 1100 | LG | A | 3 | 617.2 | 658.9 | 658.9 A (fault at 652, phase A)
671-680 | 680 | 1000 | LG | C | 3 | 635.5 | 635.5 | 635.5 A (fault at 680, phase C)
692-675 | 675 | 500 | LG | B | 3 | 711.3 | 735.0 | 735.0 A (fault at 675, phase B)
684-611 | 611 | 300 | LG | C | 3 | 622.7 | 679.4 | 679.4 A (fault at 611, phase C)
684-652 | 652 | 800 | LG | A | 3 | 617.2 | 658.9 | 658.9 A (fault at 652, phase A)

## Hand_check
Hand calculation of If,min: LG fault through Rf = 3 ohm at node 680, phase B, DG out of service
Step | Formula | Values | Result (hand) | PowerFactory | Difference
1 Thevenin sequence impedances at 680 | Z1, Z2, Z0 seen from the fault (PowerFactory, DG out) | Z1 = Z2 = 0.2860 + j0.8161 ohm; Z0 = 0.8014 + j2.1366 ohm
2 Pre-fault voltage, phase B at 680 | V_B from the load flow (complete method keeps it) | 2575.2 V at -154.95 deg (1.072 pu; regulator boost)
3 Total loop impedance | Z = Z1 + Z2 + Z0 + 3 Rf | 1.3733 + j3.7688 + 9 | 10.373 + j3.769 = 11.037 ohm at 20.0 deg
4 Fault current at 680 (LG) | I_f = 3 V_B / (Z1 + Z2 + Z0 + 3 Rf) | 3 x 2575.2 / 11.037 | 700.0 A at -174.9 deg | 701.5 A at -176.0 deg | -0.2 %
5 Load current through R2, phase B | from the load flow (before the fault) |  | 184.0 A at -164.2 deg
6 Current through R2, phase B, during the fault | I_R2 = I_load,R2 + I_f (superposition; the feeder is radial, so all of I_f passes R2) | 184.0 A at -164.2 deg + 701.5 A at -176.0 deg | 882.5 A at -173.5 deg | 878.5 A | +0.5 %
7 Load current through R1, phase B | from the load flow (before the fault) |  | 411.3 A at -173.5 deg
8 Current through R1, phase B, during the fault | I_R1 = I_load,R1 + I_f (all of I_f also passes R1) | 411.3 A at -173.5 deg + 701.5 A at -176.0 deg | 1112.5 A at -175.0 deg | 1074.4 A | +3.5 %
Why phase B gives the minimum: phase B carries the smallest load current at R1 (411 A, against 558 A on phase A and 588 A on phase C), so load + fault current is smallest on phase B.
Why the R1 hand value is about 3.5 % high: superposition with the PRE-FAULT load current assumes the loads keep drawing the same current. During the fault the phase-B voltage sags, the loads supplied through R1 draw less, and PowerFactory's complete method includes that. R1 feeds more load (632, 633, 645, 646, DL and the R2 zone) than R2, so the effect is larger at R1; at R2 the hand value is within 0.5 %.
Result: the hand calculation confirms the PowerFactory values If,min(R1) = 1074 A and If,min(R2) = 879 A within the accuracy of superposition.
Note: the R2 value is 878.5 A (rounded 879 A).